## All Trains (For Code)
| B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Total Electricity Usage [kWh/d] (including chemical production) | 14119 | 14119 | 15867 | 15684 | 14387 | 15685 | 11551 | 21366 | 20868 | 17552 | 22535 | 22535 | 20197 | 25009 | 23506 | 22935 | 21439 | 65867 | 66453 | 15473 | 20591 | 20594 | 18188.5692 | 13328.98 | 16589.3 | 16589.3 | 19620.4692 | 17984.3 | 16711.3 | 11551 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 17552 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 20197 | 24541.3 | 24541.3 | 25873.3 | 24600.3 | 65867 | 15473 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
Total Electricity Usage [kWh/d] (excluding chemical production) | 13341 | 13341 | 15089 | 14906 | 13609 | 14798 | 10578 | 20782 | 20284 | 16968 | 18756 | 18756 | 18309 | 24425 | 22642 | 19627 | 19466 | 56762 | 59478 | 14695 | 19813 | 19816 | 17410.5692 | 12463.2 | 15811.3 | 15811.3 | 18842.4692 | 17206.3 | 15933.3 | 10578 | 13565.574 | 9473.5 | 11903.5 | 10630.5 | 16968 | 22592.488 | 17363.2 | 19793.2 | 18520.2 | 18309 | 23957.3 | 23957.3 | 25095.3 | 23822.3 | 56762 | 14695 | 18830.9084 | 13589.5 | 16019.5 | 14746.5
Total Natural Gas Usage [MJ/d] (including chemical production) | 0 | 0 | 27508 | 67521 | 25909 | 15280 | 0 | 6250 | 6250 | 0 | 82506 | 84106 | 33662 | 6250 | 13428 | 116037 | 81567 | 220015 | 171261 | 0 | 0 | 0 | 6250 | 13544.1033 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 13544.1033 | 67521 | 25909 | 0 | 88756 | 96050.1033 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 13544.1033 | 67521 | 25909
Total Natural Gas Usage [MJ/d] (excluding chemical production) | 0 | 0 | 27508 | 67521 | 25909 | 6250 | 0 | 6250 | 6250 | 0 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 0 | 6250 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 0 | 0 | 67521 | 25909 | 0 | 0 | 6250 | 6250 | 67521 | 25909
CHP Electricity Generation [kWh/d] | 0 | 6310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6750 |  |  |  | 5409.77 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 4253.705 |  |  | 6512 | 6336.25
Total Imported Energy Use (excluding off-site chemical production) [MJ/d] | 48027.6 | 25311.6 | 81828.4 | 121182.6 | 74901.4 | 59522.8 | 38080.8 | 81065.2 | 79272.4 | 61084.8 | 67521.6 | 47318.4 | 65912.4 | 94180 | 87761.2 | 70657.2 | 70077.6 | 204343.2 | 220370.8 | 52902 | 71326.8 | 47037.6 | 68928.0491 | 51117.52 | 56920.68 | 37445.508 | 74082.8891 | 129463.68 | 83268.88 | 21663.9 | 55086.0664 | 40354.6 | 110373.6 | 64178.8 | 40139.1 | 87582.9568 | 68757.52 | 138776.52 | 92581.72 | 45699.3 | 86246.28 | 70932.942 | 157864.08 | 111669.28 | 180900 | 30091.5 | 74041.2702 | 55172.2 | 125191.2 | 78996.4
Total Imported Energy Use (including off-site chemical production) [MJ/d] | 50828.4 | 28112.4 | 84629.2 | 123983.4 | 77702.2 | 71746 | 41583.6 | 83167.6 | 81374.8 | 63187.2 | 163632 | 145028.8 | 106371.2 | 96282.4 | 98049.6 | 198603 | 158747.4 | 457136.2 | 410491.8 | 55702.8 | 74127.6 | 49838.4 | 71728.8491 | 61528.4313 | 59721.48 | 40246.308 | 76883.6891 | 132264.48 | 86069.68 | 25166.7 | 58588.8664 | 51467.5113 | 113876.4 | 67681.6 | 42241.5 | 183693.3568 | 172478.0313 | 234886.92 | 188692.12 | 86158.1 | 88348.68 | 73035.342 | 160664.88 | 114470.08 | 433693 | 32892.3 | 76842.0702 | 65583.1113 | 127992 | 81797.2
Total Energy Use (excluding off-site chemical production) [MJ/d] | 48027.6 | 48027.6 | 81828.4 | 121182.6 | 74901.4 | 59522.8 | 38080.8 | 81065.2 | 79272.4 | 61084.8 | 67521.6 | 67521.6 | 65912.4 | 94180 | 87761.2 | 70657.2 | 70077.6 | 204343.2 | 220370.8 | 52902 | 71326.8 | 71337.6 | 68928.0491 | 51117.52 | 56920.68 | 56920.68 | 74082.8891 | 129463.68 | 83268.88 | 38080.8 | 55086.0664 | 40354.6 | 110373.6 | 64178.8 | 61084.8 | 87582.9568 | 68757.52 | 138776.52 | 92581.72 | 65912.4 | 86246.28 | 86246.28 | 157864.08 | 111669.28 | 204343.2 | 52902 | 74041.2702 | 55172.2 | 125191.2 | 78996.4
Total Energy Use (including off-site chemical production) [MJ/d] | 50828.4 | 50828.4 | 84629.2 | 123983.4 | 77702.2 | 71746 | 41583.6 | 83167.6 | 81374.8 | 63187.2 | 163632 | 165232 | 106371.2 | 96282.4 | 98049.6 | 198603 | 158747.4 | 457136.2 | 410491.8 | 55702.8 | 74127.6 | 74138.4 | 71728.8491 | 61528.4313 | 59721.48 | 59721.48 | 76883.6891 | 132264.48 | 86069.68 | 41583.6 | 58588.8664 | 51467.5113 | 113876.4 | 67681.6 | 63187.2 | 183693.3568 | 172478.0313 | 234886.92 | 188692.12 | 106371.2 | 88348.68 | 88348.68 | 160664.88 | 114470.08 | 457136.2 | 55702.8 | 76842.0702 | 65583.1113 | 127992 | 81797.2
Note on A1: Average of COD into incinerators for B5 and B6 -Abigayle Hodson

## Typical versus Best Practice
|  | B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E | B2 | B3 | C1 | C2 | C5 | C6 | D2 | D3 | D5 | D6 | G2 | G3 | G5 | G6 | I1 | I1E | I5 | I6 | O1E | O2 | O3 | O5 | O6
Typical | Total Electricity Usage [kWh/d] | 14119 | 14119 | 15867 | 15684 | 14387 | 15685 | 11551 | 21366 | 20868 | 17552 | 22535 | 22535 | 20197 | 25009 | 23506 | 22935 | 21439 | 65867 | 66453 | 15473 | 20591 | 20594 | 18188.5692 | 13328.98 | 16589.3 | 19620.4692 | 17984.3 | 16711.3 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 24541.3 | 24541.3 | 25873.3 | 24600.3 | 15473 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
| CHP Electricity Generation [kWh/d] |  | 6310 | [9 empty] | 5612 | [9 empty] | 6750 | [15 empty] | 3568.6002 |  |  | 6048.9746
| Total Natural Gas Usage [MJ/d] | 0 | 0 | 27508 | 67521 | 25909 | 15280 | 0 | 6250 | 6250 | 0 | 82506 | 84106 | 33662 | 6250 | 13428 | 116037 | 81567 | 220015 | 171261 | 0 | 0 | 0 | 6250 | 13544.1033 | 0 | 6250 | 67521 | 25909 | 6250 | 13544.1033 | 67521 | 25909 | 88756 | 96050.1033 | 150027 | 108415 | 0 | 0 | 67521 | 25909 | 0 | 6250 | 13544.1033 | 67521 | 25909
| Total Energy Usage [MJ/d] | 50828.4 | 50828.4 | 84629.2 | 123983.4 | 77702.2 | 71746 | 41583.6 | 83167.6 | 81374.8 | 63187.2 | 163632 | 165232 | 106371.2 | 96282.4 | 98049.6 | 198603 | 158747.4 | 457136.2 | 410491.8 | 55702.8 | 74127.6 | 74138.4 | 71728.8491 | 61528.4313 | 59721.48 | 76883.6891 | 132264.48 | 86069.68 | 58588.8664 | 51467.5113 | 113876.4 | 67681.6 | 183693.3568 | 172478.0313 | 234886.92 | 188692.12 | 88348.68 | 88348.68 | 160664.88 | 114470.08 | 55702.8 | 76842.0702 | 65583.1113 | 127992 | 81797.2
Best Practice | Total Electricity Usage [kWh/d] | 9479 | 9479 | 10748 | 12135 | 10792 | 11134 | 8903 | 14355 | 13531 | 11333 | 15645 | 15645 | 13226 | 15102 | 14347 | 15359 | 14199 | 37255 | 36734 | 12300 | 13409 | 13408 | 12293.3477 | 9670.8143 | 10956.8571 | 13174.1007 | 13540.8571 | 12227.8571 | 11411.6561 | 9040.3143 | 11488 | 10175 | 18574.0781 | 15748.8143 | 18196.5 | 16883.5 | 14049.8571 | 14049.8571 | 16813.8571 | 15500.8571 | 12300 | 15179.8419 | 12436.3143 | 14884 | 13571
| CHP Electricity Generation [kWh/d] |  | 8100 | [9 empty] | 7850 | [9 empty] | 8180 | [15 empty] | 0 |  |  | 7821.0633
| Total Natural Gas Usage [MJ/d] | 0 | 0 | 0 | 42414 | 5952 | 15064 | 0 | 5952 | 5952 | 0 | 96257 | 96257 | 41583 | 5952 | 13212 | 119845 | 87898 | 220015 | 143461 | 0 | 0 | 0 | 5952 | 13209.1076 | 0 | 5952 | 42414 | 5952 | 5952 | 13209.1076 | 42414 | 5952 | 102209 | 109466.1076 | 138671 | 102209 | 0 | 0 | 42414 | 5952 | 0 | 5952 | 13209.1076 | 42414 | 5952
| Total Energy Usage [MJ/d] | 34124.4 | 34124.4 | 38692.8 | 86100 | 44803.2 | 55146.4 | 32050.8 | 57630 | 54663.6 | 40798.8 | 152579 | 152579 | 89196.6 | 60319.2 | 64861.2 | 175137.4 | 139014.4 | 354133 | 275703.4 | 44280 | 48272.4 | 48268.8 | 50208.0517 | 48024.0389 | 39444.6857 | 53378.7627 | 91161.0857 | 49972.2857 | 47033.9621 | 45754.2389 | 83770.8 | 42582 | 169075.6812 | 166161.8389 | 204178.4 | 162989.6 | 50579.4857 | 50579.4857 | 102943.8857 | 61755.0857 | 44280 | 60599.4308 | 57979.8389 | 95996.4 | 54807.6

## Sensitivity Analysis
|  | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Low Values | Total Electricity Usage [kWh/d] | 17561.3088 | 13284.7264 | 16589.3 | 16589.3 | 19216.6919 | 17984.3 | 16711.3 | 11551 | 14152.0366 | 10490.0264 | 12876.5 | 11603.5 | 17552 | 25712.54 | 21185.7264 | 23572.2 | 22299.2 | 20197 | 24183.3 | 24183.3 | 25873.3 | 24600.3 | 65867 | 15473 | 18946.9056 | 14411.0264 | 16797.5 | 15524.5
| CHP Electricity Generation [kWh/d] |  |  |  | 4504.935 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 1915.675 |  |  | 6512 | 6336.25
| Net Electricity Import [kWh/d] | 17561.3088 | 13284.7264 | 16589.3 | 12084.365 | 19216.6919 | 17984.3 | 16711.3 | 6990.75 | 14152.0366 | 10490.0264 | 12876.5 | 11603.5 | 11733.75 | 25712.54 | 21185.7264 | 23572.2 | 22299.2 | 14582.25 | 24183.3 | 22267.625 | 25873.3 | 24600.3 | 59355 | 9136.75 | 18946.9056 | 14411.0264 | 16797.5 | 15524.5
| Total Natural Gas Usage [MJ/d] | 6250 | 11613.1679 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 11613.1679 | 67521 | 25909 | 0 | 88756 | 94119.1679 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 11613.1679 | 67521 | 25909
| Total Energy Usage (Low) [MJ/d] | 69470.7118 | 59438.1828 | 59721.48 | 59721.48 | 75430.0909 | 132264.48 | 86069.68 | 41583.6 | 57197.3317 | 49377.2628 | 113876.4 | 67681.6 | 63187.2 | 181321.1439 | 170387.7828 | 234886.92 | 188692.12 | 106371.2 | 87059.88 | 87059.88 | 160664.88 | 114470.08 | 457136.2 | 55702.8 | 74458.8601 | 63492.8628 | 127992 | 81797.2
High Values | Total Electricity Usage [kWh/d] | 18814.8296 | 13388.4172 | 16947.3 | 16947.3 | 20023.2465 | 17984.3 | 16711.3 | 11551 | 14924.1114 | 10593.7172 | 12876.5 | 11603.5 | 17552 | 27029.436 | 21289.4172 | 23572.2 | 22299.2 | 20197 | 24541.3 | 24541.3 | 25873.3 | 24600.3 | 65867 | 15473 | 20269.9112 | 14514.7172 | 16797.5 | 15524.5
| CHP Electricity Generation [kWh/d] |  |  |  | 6314.6975 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 6591.735 |  |  | 6512 | 6336.25
| Net Electricity Import [kWh/d] | 18814.8296 | 13388.4172 | 16947.3 | 10632.6025 | 20023.2465 | 17984.3 | 16711.3 | 6990.75 | 14924.1114 | 10593.7172 | 12876.5 | 11603.5 | 11733.75 | 27029.436 | 21289.4172 | 23572.2 | 22299.2 | 14582.25 | 24541.3 | 17949.565 | 25873.3 | 24600.3 | 59355 | 9136.75 | 20269.9112 | 14514.7172 | 16797.5 | 15524.5
| Total Natural Gas Usage [MJ/d] | 6250 | 16740.6584 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 16740.6584 | 67521 | 25909 | 0 | 88756 | 99246.6584 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 16740.6584 | 67521 | 25909
| Total Energy Usage (High) [MJ/d] | 73983.3864 | 64938.9603 | 61010.28 | 61010.28 | 78333.6874 | 132264.48 | 86069.68 | 41583.6 | 59976.8011 | 54878.0403 | 113876.4 | 67681.6 | 63187.2 | 186061.9697 | 175888.5603 | 234886.92 | 188692.12 | 106371.2 | 88348.68 | 88348.68 | 160664.88 | 114470.08 | 457136.2 | 55702.8 | 79221.6804 | 68993.6403 | 127992 | 81797.2
Selected Values | Total Electricity Usage [kWh/d] | 18188.5692 | 13328.98 | 16589.3 | 16589.3 | 19620.4692 | 17984.3 | 16711.3 | 11551 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 17552 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 20197 | 24541.3 | 24541.3 | 25873.3 | 24600.3 | 65867 | 15473 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
| CHP Electricity Generation [kWh/d] |  |  |  | 5409.77 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 4253.705 |  |  | 6512 | 6336.25
| Net Electricity Import [kWh/d] | 18188.5692 | 13328.98 | 16589.3 | 11179.53 | 19620.4692 | 17984.3 | 16711.3 | 6990.75 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 11733.75 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 14582.25 | 24541.3 | 20287.595 | 25873.3 | 24600.3 | 59355 | 9136.75 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
| Total Natural Gas Usage [MJ/d] | 6250 | 13544.1033 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 13544.1033 | 67521 | 25909 | 0 | 88756 | 96050.1033 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 13544.1033 | 67521 | 25909
| Total Energy Usage (Selected) [MJ/d] | 71728.8491 | 61528.4313 | 59721.48 | 59721.48 | 76883.6891 | 132264.48 | 86069.68 | 41583.6 | 58588.8664 | 51467.5113 | 113876.4 | 67681.6 | 63187.2 | 183693.3568 | 172478.0313 | 234886.92 | 188692.12 | 106371.2 | 88348.68 | 88348.68 | 160664.88 | 114470.08 | 457136.2 | 55702.8 | 76842.0702 | 65583.1113 | 127992 | 81797.2

## WERF Trains (Electricity)
All values in kWh/day | B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E
Electricity Usage by Process
Liquid Stream Processes | 8834 | 8834 | 8834 | 9001 | 8977 | 11321 | 6348 | 13830 | 11471 | 12266 | 16890 | 16890 | 14551 | 18915 | 19210 | 17287 | 15791 | 60373 | 58485 | 10269 | 15321 | 15324
Influent Pump Station | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2568 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096
Screening and Grit Removal | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
Primary Clarifiers | 100 | 100 | 100 | 101 | 101 |  | 102 |  | 101 | 101 | 101 | 101 | 104 |  |  | 101 | 101 | 102 |  | 102
Biological Reactor Blowers | 4200 | 4200 | 4200 | 4359 | 4335 | 6737 |  | 9439 | 7036 | 7830 | 9625 | 9625 | 9179 | 14538 | 14639 | 9465 | 9309 | 47907 | 48251 | 5628 | 9584 | 9587
Final Clarifiers + RAS Pumping | 1021 | 1021 | 1021 | 1028 | 1028 | 1071 | 93 | 1072 | 1015 | 1016 | 650 | 650 | 645 | 1058 | 1058 | 663 | 658 |  |  | 1026 | 2224 | 2224
Trickling Filter | [6 empty] | 1344
TF Recycle Pump | [6 empty] | 629
MBR Effluent Pump | [17 empty] | 524 | 524
Denite Filter | [15 empty] | 1015 | 1015
Disinfection | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Hypochlorite Production | 778 | 778 | 778 | 778 | 778 | 778 | 973 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 778 | 584 | 584 | 584 | 584 | 778 | 778 | 778
Acetic Acid Production | [10 empty] | 3195 | 3195 | 1304 |  |  | 2724 | 1389 | 8521 | 6391
Solids Processes | 1485 | 1485 | 3233 | 2883 | 1610 | 564 | 1403 | 3736 | 5597 | 1486 | 1845 | 1845 | 1846 | 2294 | 496 | 1848 | 1848 | 1694 | 4168 | 1404 | 1470 | 1470
Gravity Thickener | 23 | 23 | 23 | 25 | 25 |  | 26 |  | 25 | 23 | 23 | 23 | 25 |  |  | 25 | 26 | 30 |  | 27
Mechanical Thickener | 156 | 156 | 156 | 157 | 157 | 163 |  | 161 | 156 | 157 | 158 | 158 | 157 | 160 | 160 | 159 | 158 |  | 164 |  | 164 | 164
Anaerobic Digestion | 1217 | 1217 | 1217 |  |  |  | 1288 |  |  | 1217 | 1575 | 1575 | 1575 |  |  | 1575 | 1575 | 1575 |  | 1288 | 1217 | 1217
Aerobic Digestion | [7 empty] | 3486 | 5327 |  |  |  |  | 2045 |  |  |  |  | 3915
Dewatering | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Sidestream Pump
Incineration |  |  |  | 2612 | 1339
Dryer |  |  | 1748
Lime Stabilization | [5 empty] | 203 | [8 empty] | 161
Lime Production | [5 empty] | 109 | [8 empty] | 86
Plant-wide | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
Odor Control | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Site Lighting & Misc. | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
Total Electricity Usage (including chemical production) | 14119 | 14119 | 15867 | 15684 | 14387 | 15685 | 11551 | 21366 | 20868 | 17552 | 22535 | 22535 | 20197 | 25009 | 23506 | 22935 | 21439 | 65867 | 66453 | 15473 | 20591 | 20594
CHP Electricity Generation |  | 6310 | [9 empty] | 5612 | [9 empty] | 6750
Net Electricity Import | 14119 | 7809 | 15867 | 15684 | 14387 | 15685 | 11551 | 21366 | 20868 | 17552 | 22535 | 16923 | 20197 | 25009 | 23506 | 22935 | 21439 | 65867 | 66453 | 15473 | 20591 | 13844
Total Electricity Usage (excluding chemical production) | 13341 | 13341 | 15089 | 14906 | 13609 | 14798 | 10578 | 20782 | 20284 | 16968 | 18756 | 18756 | 18309 | 24425 | 22642 | 19627 | 19466 | 56762 | 59478 | 14695 | 19813 | 19816

## Frankentrains (Electricity)
All values in kWh/day | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Electricity Usage by Process
Liquid Stream Processes | 8834 | 8989 | 11321 | 11321 | 11321 | 11321 | 11321 | 6348 | 6348 | 6348 | 6348 | 6348 | 12266 | 16890 | 16890 | 16890 | 16890 | 14551 | 18915 | 18915 | 19210 | 19210 | 60373 | 10269 | 10269 | 10269 | 10269 | 10269
Influent Pump Station | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2568 | 2568 | 2568 | 2568 | 2568 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096
Screening and Grit Removal | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
Primary Clarifiers | 100 | 101 | [5 empty] | 102 | 102 | 102 | 102 | 102 | 101 | 101 | 101 | 101 | 101 | 104 |  |  |  |  | 102 | 102 | 102 | 102 | 102 | 102
Biological Reactor Blowers | 4200 | 4347 | 6737 | 6737 | 6737 | 6737 | 6737 | [5 empty] | 7830 | 9625 | 9625 | 9625 | 9625 | 9179 | 14538 | 14538 | 14639 | 14639 | 47907 | 5628 | 5628 | 5628 | 5628 | 5628
Final Clarifiers + RAS Pumping | 1021 | 1028 | 1071 | 1071 | 1071 | 1071 | 1071 | 93 | 93 | 93 | 93 | 93 | 1016 | 650 | 650 | 650 | 650 | 645 | 1058 | 1058 | 1058 | 1058 |  | 1026 | 1026 | 1026 | 1026 | 1026
Trickling Filter | [7 empty] | 1344 | 1344 | 1344 | 1344 | 1344
TF Recycle Pump | [7 empty] | 629 | 629 | 629 | 629 | 629
MBR Effluent Pump | [22 empty] | 524
Denite Filter
Disinfection | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Hypochlorite Production | 778 | 778 | 778 | 778 | 778 | 778 | 778 | 973 | 973 | 973 | 973 | 973 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 778 | 778 | 584 | 778 | 778 | 778 | 778 | 778
Acetic Acid Production | [13 empty] | 3195 | 3195 | 3195 | 3195 | 1304 |  |  |  |  | 8521
Solids Processes | 5554.5692 | 539.98 | 1468.3 | 1468.3 | 4499.4692 | 2863.3 | 1590.3 | 1403 | 4390.574 | 386.28 | 2728.5 | 1455.5 | 1486 | 5681.488 | 539.98 | 2882.2 | 1609.2 | 1846 | 1826.3 | 1826.3 | 2863.3 | 1590.3 | 1694 | 1404 | 5539.9084 | 386.28 | 2728.5 | 1455.5
Gravity Thickener | 24.1 | 24.1 | [5 empty] | 26 |  | 27.5 | 27.5 | 27.5 | 23 | 24.1 | 24.1 | 24.1 | 24.1 | 25 |  |  |  |  | 30 | 27 | 27.5 | 27.5 | 27.5 | 27.5
Mechanical Thickener | 157.1 | 157.1 | 162.3 | 162.3 | 162.3 | 162.3 | 162.3 |  | 162.3 |  |  |  | 157 | 157.1 | 157.1 | 157.1 | 157.1 | 157 | 162.3 | 162.3 | 162.3 | 162.3
Anaerobic Digestion |  |  | 1217 | 1217 |  |  |  | 1288 |  |  |  |  | 1217 |  |  |  |  | 1575 | 1575 | 1575 |  |  | 1575 | 1288
Aerobic Digestion | 5284.3692 |  |  |  | 4248.1692 |  |  |  | 4139.274 |  |  |  |  | 5411.288 | [10 empty] | 5423.4084
Dewatering | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Sidestream Pump
Incineration | [5 empty] | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  |  | 2612 | 1339
Dryer
Lime Stabilization |  | 182 | [7 empty] | 182 |  |  |  |  | 182 | [10 empty] | 182
Lime Production |  | 87.78 | [7 empty] | 87.78 |  |  |  |  | 87.78 | [10 empty] | 87.78
Plant-wide | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
Odor Control | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Site Lighting & Misc. | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
Total Electricity Usage | 18188.5692 | 13328.98 | 16589.3 | 16589.3 | 19620.4692 | 17984.3 | 16711.3 | 11551 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 17552 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 20197 | 24541.3 | 24541.3 | 25873.3 | 24600.3 | 65867 | 15473 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
CHP Electricity Generation |  |  |  | 5409.77 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 4253.705 |  |  | 6512 | 6336.25
Net Electricity Import | 18188.5692 | 13328.98 | 16589.3 | 11179.53 | 19620.4692 | 17984.3 | 16711.3 | 6990.75 | 14538.574 | 10534.28 | 12876.5 | 11603.5 | 11733.75 | 26371.488 | 21229.98 | 23572.2 | 22299.2 | 14582.25 | 24541.3 | 20287.595 | 25873.3 | 24600.3 | 59355 | 9136.75 | 19608.9084 | 14455.28 | 16797.5 | 15524.5
Total Electricity Usage (excluding chemical production) | 17410.5692 | 12463.2 | 15811.3 | 15811.3 | 18842.4692 | 17206.3 | 15933.3 | 10578 | 13565.574 | 9473.5 | 11903.5 | 10630.5 | 16968 | 22592.488 | 17363.2 | 19793.2 | 18520.2 | 18309 | 23957.3 | 23957.3 | 25095.3 | 23822.3 | 56762 | 14695 | 18830.9084 | 13589.5 | 16019.5 | 14746.5
Note on B1: Use B1 for liquids + E2P for solids + calculate AeD energy use using CODin from B1 -Abigayle Hodson _Marked as resolved_ -Sahar El Abbadi _Re-opened_ -Sahar El Abbadi B1 / B4 (identical) for liquids + AeD energy calculated from CODin B1 + average thickener values for gravity + mechanical configuration -Sahar El Abbadi
Note on C1: Use averaged of B5 and B6 for liquids and solids except for incineration (no longer relevant) and lime production/stabilization, which was calculated using average dosing rate. -Abigayle Hodson Update to reflect the average value used for lime production instead of dosing -Sahar El Abbadi Average B5 and B6 for liquids; Lime production: energy based on average dosing rate; lime stabilization process energy using average of C3 and I3; average thickener values for gravity + mechanical thickener -Sahar El Abbadi
Note on D1: Use C3 for liquids + B1 for solids- modified gravity thickener -Abigayle Hodson Liquids: C3 Solids: B1 cluster for anaerobic digestion (B1 / B1E/F1, P1, P1E have identical energy for anaerobic digestion) Average thickener values for mechanical thickener only present -Sahar El Abbadi
Note on E1: Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on F1: Use C3 for liquids + N2 for solids + calculate AeD energy use using CODin from C3 -Abigayle Hodson Liquid: C3 Solids: AeD energy calculated using CODin from C3 as input to linear regression; thickener values average for mechanical thickener only present -Sahar El Abbadi
Note on G1: Use C3 for liquids and B5 for solids- modified gravity thickener -Abigayle Hodson
Note on H1: Use C3 for liquids and B6 for solids- modified thickener values -Abigayle Hodson
Note on I1: Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on J1: Use D1 for liquids + N2 for solids + calculate AeD energy use using CODin from D1 -Abigayle Hodson Liquids: D1 Solids: AeD energy calculated using CODin from D1 as input for linear regression Thickener average values for mechanical thickener only present -Sahar El Abbadi
Note on K1: Use D1 for liquids and an average of D5 and D6 for solids, excluding incineration (no longer relevant) and lime production/stabilization (calculated using average dosing rate) -Abigayle Hodson Liquids: D1 Solids: lime production energy is calculated using average dosing rate Lime stabilization energy is average of I3 and C3; thickener is average value for gravity thickener only -Sahar El Abbadi
Note on L1: Use D1 for liquids and B5 for solids- modified thickener values -Abigayle Hodson
Note on M1: Use D1 for liquids and B6 for solids- modified thickener values -Abigayle Hodson
Note on N1: Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on O1: Use G1 for liquids + E2P for solids + calculate AeD energy use from CODin from G1 -Abigayle Hodson Liquid: G1 Solids: AeD calculated using CODin from G1 Thickener: modified value for average with gravity + mechanical both present -Sahar El Abbadi
Note on P1: Use G1 for liquids + average of G5 and G6 for solids, excluding incineration (no longer relevant) and lime production/stabilization (calculated using average dosing rate) -Abigayle Hodson Liquids: G1/G1E Solids: Lime production energy calculated using average dosing rate Lime stabilization process energy using average of C3 and I3 Average thickener values for gravity + mechanical thickeners present -Sahar El Abbadi
Note on Q1: Use G1 for liquids and B5 for solids -Abigayle Hodson G1 for liquids; B5 for solids with modified thickener values (average of gravity + mechanical present) -Sahar El Abbadi
Note on R1: Use G1 for liquids + B6 for solids -Abigayle Hodson G1 for liquids; B6 for solids with modified thickener values (average of gravity + mechanical present) -Sahar El Abbadi
Note on S1: Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on T1: Use I2 for liquids + G1 for solids with AnD from nutrient removal cluster. modified thickener -Abigayle Hodson Note: calling the G1/G1E/H1/N1 the "Nutrient removal cluster" for anaerobic digestion energy -Sahar El Abbadi
Note on U1: Use I2 for liquids + G1E for solids, modified thickener -Abigayle Hodson Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on V1: Use I3 for liquids and B5 for solids- modified gravity thickener -Abigayle Hodson
Note on W1: Use I3 for liquids and B6 for solids- modified gravity thickener -Abigayle Hodson
Note on X1: Electricity generated based on biogas production and generator efficiency of 0.0925 -Abigayle Hodson
Note on Y1: Use O1 for liquids and O1 for solids processing -Abigayle Hodson Energy production from B1E -Sahar El Abbadi Electricity generation based on biogas yield and generator efficiency of 0.0925 -Abigayle Hodson
Note on Z1: Use O1 for liquids + E2P for solids + calculate AeD energy use using CODin from O1, modified thickener -Abigayle Hodson Liquid: O1 Solid: AeD energy calculated using O1 CODin as input for linear regression Thickener average values for gravity thickener only present -Sahar El Abbadi
Note on AA1: Use O1 for liquids + average of O5 and O6 for solids, excluding incineration (no longer relevant) and lime produciton/stabilization (calculated using average dosing rate) -Abigayle Hodson Liquid: O1 Solid: Lime production energy calculated using average dosing rate Lime stabilization process energy using average of C3 and I3 Thickener average values for gravity thickener only present -Sahar El Abbadi
Note on AB1: Use O1 for liquids and B5 for solids, modified thickener -Abigayle Hodson Liquid: O1 Solids: B5 for incinerator Thickener average values for gravity thickener only present -Sahar El Abbadi
Note on AC1: Use O1 for liquids and B6 for solids, modified thickener -Abigayle Hodson B6 for incinerator Thickener average values for gravity thickener only present -Sahar El Abbadi
Note on B18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on C18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on K18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on L18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on M18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on O18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on P18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Q18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on R18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Z18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AA18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AB18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AC18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on B19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on C19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on D19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on F19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on G19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on H19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on J19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on O19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on P19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Q19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on R19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on T19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on U19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on V19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on W19: Average energy requirement for mechanical thickeners in treatment trains that do not have a gravity thickener -Abigayle Hodson
Note on C26: Use average of lime stabilization values for C3 and I3 -Abigayle Hodson
Note on K26: Use average of lime stabilization values for C3 and I3 -Abigayle Hodson
Note on P26: Use average of lime stabilization values for C3 and I3 -Abigayle Hodson
Note on AA26: Use average of lime stabilization values for C3 and I3 -Abigayle Hodson
Note on C27: Average electricity use for lime production -Abigayle Hodson
Note on K27: Average electricity use for lime production -Abigayle Hodson
Note on P27: Average electricity use for lime production -Abigayle Hodson
Note on AA27: Average electricity use for lime production -Abigayle Hodson

## Frankentrains (Electricity) SA
All values in kWh/day | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Electricity Usage by Process
Liquid Stream Processes | 8834 | 8989 | 11321 | 11321 | 11321 | 11321 | 11321 | 6348 | 6348 | 6348 | 6348 | 6348 | 12266 | 16890 | 16890 | 16890 | 16890 | 14551 | 18915 | 18915 | 19210 | 19210 | 60373 | 10269 | 10269 | 10269 | 10269 | 10269
Influent Pump Station | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2568 | 2568 | 2568 | 2568 | 2568 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096 | 2096
Screening and Grit Removal | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
Primary Clarifiers | 100 | 101 | [5 empty] | 102 | 102 | 102 | 102 | 102 | 101 | 101 | 101 | 101 | 101 | 104 |  |  |  |  | 102 | 102 | 102 | 102 | 102 | 102
Biological Reactor Blowers | 4200 | 4347 | 6737 | 6737 | 6737 | 6737 | 6737 | [5 empty] | 7830 | 9625 | 9625 | 9625 | 9625 | 9179 | 14538 | 14538 | 14639 | 14639 | 47907 | 5628 | 5628 | 5628 | 5628 | 5628
Final Clarifiers + RAS Pumping | 1021 | 1028 | 1071 | 1071 | 1071 | 1071 | 1071 | 93 | 93 | 93 | 93 | 93 | 1016 | 650 | 650 | 650 | 650 | 645 | 1058 | 1058 | 1058 | 1058 |  | 1026 | 1026 | 1026 | 1026 | 1026
Trickling Filter | [7 empty] | 1344 | 1344 | 1344 | 1344 | 1344
TF Recycle Pump | [7 empty] | 629 | 629 | 629 | 629 | 629
MBR Effluent Pump | [22 empty] | 524
Denite Filter
Disinfection | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Hypochlorite Production | 778 | 778 | 778 | 778 | 778 | 778 | 778 | 973 | 973 | 973 | 973 | 973 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 778 | 778 | 584 | 778 | 778 | 778 | 778 | 778
Acetic Acid Production | [13 empty] | 3195 | 3195 | 3195 | 3195 | 1304 |  |  |  |  | 8521
Solids Processes | 4927.3088 | 495.7264 | 1468.3 | 1468.3 | 4095.6919 | 2863.3 | 1590.3 | 1403 | 4004.0366 | 342.0264 | 2728.5 | 1455.5 | 1486 | 5022.54 | 495.7264 | 2882.2 | 1609.2 | 1846 | 1468.3 | 1468.3 | 2863.3 | 1590.3 | 1694 | 1404 | 4877.9056 | 342.0264 | 2728.5 | 1455.5
Gravity Thickener | 24.1 | 24.1 | [5 empty] | 26 |  | 27.5 | 27.5 | 27.5 | 23 | 24.1 | 24.1 | 24.1 | 24.1 | 25 |  |  |  |  | 30 | 27 | 27.5 | 27.5 | 27.5 | 27.5
Mechanical Thickener | 157.1 | 157.1 | 162.3 | 162.3 | 162.3 | 162.3 | 162.3 |  | 162.3 |  |  |  | 157 | 157.1 | 157.1 | 157.1 | 157.1 | 157 | 162.3 | 162.3 | 162.3 | 162.3
Anaerobic Digestion |  |  | 1217 | 1217 |  |  |  | 1288 |  | 0 |  |  | 1217 |  |  |  |  | 1575 | 1217 | 1217 |  |  | 1575 | 1288
Aerobic Digestion | 4657.1088 |  |  |  | 3844.3919 |  |  |  | 3752.7366 | 0 |  |  |  | 4752.34 | [10 empty] | 4761.4056
Dewatering | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Sidestream Pump | [9 empty] | 0
Incineration | [5 empty] | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  | 2612 | 1339 |  |  |  |  | 2612 | 1339
Dryer
Lime Stabilization |  | 161 | [7 empty] | 161 |  |  |  |  | 161 | [10 empty] | 161
Lime Production |  | 64.5264 | [7 empty] | 64.5264 |  |  |  |  | 64.5264 | [10 empty] | 64.5264
Plant-wide | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
Odor Control | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Site Lighting & Misc. | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
Total Electricity Usage | 17561.3088 | 13284.7264 | 16589.3 | 16589.3 | 19216.6919 | 17984.3 | 16711.3 | 11551 | 14152.0366 | 10490.0264 | 12876.5 | 11603.5 | 17552 | 25712.54 | 21185.7264 | 23572.2 | 22299.2 | 20197 | 24183.3 | 24183.3 | 25873.3 | 24600.3 | 65867 | 15473 | 18946.9056 | 14411.0264 | 16797.5 | 15524.5
CHP Electricity Generation |  |  |  | 4504.935 |  |  |  | 4560.25 |  |  |  |  | 5818.25 |  |  |  |  | 5614.75 |  | 1915.675 |  |  | 6512 | 6336.25
Net Electricity Import | 17561.3088 | 13284.7264 | 16589.3 | 12084.365 | 19216.6919 | 17984.3 | 16711.3 | 6990.75 | 14152.0366 | 10490.0264 | 12876.5 | 11603.5 | 11733.75 | 25712.54 | 21185.7264 | 23572.2 | 22299.2 | 14582.25 | 24183.3 | 22267.625 | 25873.3 | 24600.3 | 59355 | 9136.75 | 18946.9056 | 14411.0264 | 16797.5 | 15524.5
Note on B1: Use B1 for liquids + average thickener values for trains with both gravity and mechanical thickeners, AeD based on influent COD (lower) -Abigayle Hodson
Note on C1: Use averaged of B5 and B6 for liquids and solids except for incineration (no longer relevant) and lime production/stabilization from TT w/ lowest energy use (B1 and I3), average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on D1: Use C3 for liquids (excluding lime), B1 for solids, and TT w/ lowest AnD energy use for AnD (B1), modified thickeners -Abigayle Hodson
Note on E1: Electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on F1: Use C3 for liquids (minus lime) + AeD based on influent COD (lower), modified thickeners -Abigayle Hodson
Note on G1: Use C3 for liquids (minus lime) and B5 for solids, modified thickener- don't include in SA -Abigayle Hodson
Note on H1: Use C3 for liquids (minus lime) and B6 for solids, modified thickener- don't include in SA -Abigayle Hodson
Note on I1: Electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on J1: Use D1 for liquids, AeD based on influent COD (lower) + modified thickeners -Abigayle Hodson
Note on K1: Use D1 for liquids and an average of D5 and D6 for solids, excluding incineration (no longer relevant) and lime production/stabilization from TT w/ lowest energy use (B1 and I3) -Abigayle Hodson
Note on L1: Use D1 for liquids and B5 for solids, modified thickener -Abigayle Hodson Do not include in SA -Abigayle Hodson
Note on M1: Use D1 for liquids and B6 for solids, modified thickener -Abigayle Hodson Do not include in SA -Abigayle Hodson
Note on N1: Electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on O1: Use G1 for liquids + modified thickeners, AeD calculated based on influent COD (lower) -Abigayle Hodson
Note on P1: Use G1 for liquids + average of G5 and G6 for solids, excluding incineration (no longer relevant) and lime production/stabilization from TT w/ lowest energy use (B1 and I3) -Abigayle Hodson
Note on Q1: Use G1 for liquids and B5 for solids + modified thickeners -Abigayle Hodson Don't include in SA -Abigayle Hodson
Note on R1: Use G1 for liquids + B6 for solids + modified thickeners -Abigayle Hodson Don't include in SA -Abigayle Hodson
Note on S1: Electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on T1: Use I2 for liquids + G1 for solids + AnD w/ lowest energy use (B1), modified thickener -Abigayle Hodson
Note on U1: Use I2 for liquids + G1E for solids + AnD w/ lowest energy use (B1E), modified thickener, electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on V1: Use I3 for liquids (minus lime) and B5 for solids, modified thickener -Abigayle Hodson
Note on W1: Use I3 for liquids (minus lime) and B6 for solids, modified thickener -Abigayle Hodson
Note on X1: Electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson
Note on Y1: Use O1 for liquids and O1 for solids processing, electricity generated based on biogas production (low) and generator efficiency of 0.0925 -Abigayle Hodson Don't use in SA -Abigayle Hodson
Note on Z1: Use O1 for liquids, modified thickener, AeD based on influent COD linear regression (low) -Abigayle Hodson
Note on AA1: Use O1 for liquids + average of O5 and O6 for solids, excluding incineration (no longer relevant) and lime production/stabilization from TT w/ lowest energy use (B1 and I3) -Abigayle Hodson
Note on AB1: Use O1 for liquids and B5 for solids, modified thickener values -Abigayle Hodson Don't include in SA -Abigayle Hodson
Note on AC1: Use O1 for liquids and B6 for solids, modified thickener values -Abigayle Hodson Don't include in SA -Abigayle Hodson
Note on B18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on C18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on K18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on L18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on M18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on O18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on P18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Q18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on R18: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Z18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AA18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AB18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on AC18: Use average gravity thickener value for trains w/ gravity thickener and w/out mechanical thickener -Abigayle Hodson
Note on B19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on C19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on D19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on F19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on G19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on H19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on J19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on O19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on P19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on Q19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on R19: Average thickener values for trains with both gravity and mechanical thickeners -Abigayle Hodson
Note on T19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on U19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on V19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson
Note on W19: Use average mechanical thickener value from trains w/ mechanical thickener and w/out gravity thickener -Abigayle Hodson

## WERF Trains (Natural Gas)
| B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E
All values in MJ/d
DG to CHP | 0 | 68300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73000
DG to Boiler | 28625 | 0 | 28625 | 0 | 0 | 0 | 28500 | 0 | 0 | 29625 | 32750 | 1600 | 34250 | 0 | 0 | 38000 | 37250 | 37125 | 0 | 30375 | 30375 | 0
NG to Boiler | 0 | 0 | 0 | 6250 | 6250 | 6250 | 0 | 6250 | 6250 | 0 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 0 | 6250 | 0 | 0 | 0
Fuel Used for Chemical Production (Acetic Acid) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82506 | 82506 | 33662 | 0 | 0 | 70342 | 35874 | 220015 | 165011 | 0 | 0 | 0
Fuel Used for Chemical Production (Methanol) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45695 | 45693 | 0 | 0 | 0 | 0 | 0
Fuel Used for Chemical Production (Lime) | 0 | 0 | 0 | 0 | 0 | 9030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7178 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Natural Gas to Direct Dryer | 0 | 0 | 27508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Natural Gas to Incinerator | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Natural Gas Usage (including chemical production) [MJ/d] | 0 | 0 | 27508 | 67521 | 25909 | 15280 | 0 | 6250 | 6250 | 0 | 82506 | 84106 | 33662 | 6250 | 13428 | 116037 | 81567 | 220015 | 171261 | 0 | 0 | 0
Total Natural Gas Usage (excluding chemical production) [MJ/d] | 0 | 0 | 27508 | 67521 | 25909 | 6250 | 0 | 6250 | 6250 | 0 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 0 | 6250 | 0 | 0 | 0
Note on M1: Substitute natural gas for biogas in boiler- results in decreased electricity production -Abigayle Hodson

## Frankentrains (Natural Gas)
| B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
All values in MJ/d
DG to CHP | 0 | 0 | 0 | 58484 | 0 | 0 | 0 | 49300 | 0 | 0 | 0 | 0 | 62900 | 0 | 0 | 0 | 0 | 60700 | 0 | 45986 | 0 | 0 | 70400 | 68500 | 0 | 0 | 0 | 0
DG to Boiler | 0 | 0 | 28625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NG to Boiler | 6250 | 6250 | 0 | 0 | 6250 | 6250 | 6250 | 0 | 6250 | 6250 | 6250 | 6250 | 0 | 6250 | 6250 | 6250 | 6250 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 6250 | 6250 | 6250 | 6250
Fuel Used for Chemical Production (Acetic Acid) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82506 | 82506 | 82506 | 82506 | 33662 | 0 | 0 | 0 | 0 | 220015 | 0 | 0 | 0 | 0 | 0
Fuel Used for Chemical Production (Methanol) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel Used for Chemical Production (Lime) | 0 | 7294.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7294.1033 | 0 | 0 | 0 | 0 | 7294.1033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7294.1033 | 0 | 0
Natural Gas to Direct Dryer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Natural Gas to Incinerator | 0 | 0 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 0 | 61271 | 19659
Total Natural Gas Usage | 6250 | 13544.1033 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 13544.1033 | 67521 | 25909 | 0 | 88756 | 96050.1033 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 13544.1033 | 67521 | 25909
Imported Natural Gas, including chemicals | 6250 | 13544.1033 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 13544.1033 | 67521 | 25909 | 0 | 88756 | 96050.1033 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 13544.1033 | 67521 | 25909
Imported Natural Gas, excluding chemicals | 6250 | 6250 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 0 | 0 | 67521 | 25909 | 0 | 0 | 6250 | 6250 | 67521 | 25909
Note on B1: Use B1 for liquids + E2P for solids -Abigayle Hodson
Note on C1: Use averaged of B5 and B6 for liquids and solids except for incineration (no longer relevant) and lime stabilization, which was calculated using average dosing rate. -Abigayle Hodson
Note on D1: Use C3 for liquids (minus lime) + B1 for solids -Abigayle Hodson
Note on E1: Use C1 for liquids + calculate biogas based on influent COD linear regression, assume all DG goes to CHP -Abigayle Hodson
Note on F1: Use C3 for liquids (minus lime)+ N2 for solids -Abigayle Hodson
Note on G1: Use C3 for liquids (minus lime) and B5 for solids- modified gravity thickener -Abigayle Hodson
Note on H1: Use C3 for liquids (minus lime) and B6 for solids- modified thickener values -Abigayle Hodson
Note on I1: Use D1 for liquids + biogas, assume all biogas goes to CHP -Abigayle Hodson
Note on J1: Use D1 for liquids + N2 for solids -Abigayle Hodson
Note on K1: Use D1 for liquids and an average of D5 and D6 for solids, excluding incineration (no longer relevant) and lime stabilization (calculated using average dosing rate) -Abigayle Hodson
Note on L1: Use D1 for liquids and B5 for solids -Abigayle Hodson
Note on M1: Use D1 for liquids and B6 for solids -Abigayle Hodson
Note on N1: Use F1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on O1: Use G1 for liquids + E2P for solids -Abigayle Hodson
Note on P1: Use G1 for liquids + average of G5 and G6 for solids, excluding incineration (no longer relevant) and lime stabilization (calculated using average dosing rate) -Abigayle Hodson
Note on Q1: Use G1 for liquids and B5 for solids -Abigayle Hodson
Note on R1: Use G1 for liquids + B6 for solids -Abigayle Hodson
Note on S1: Use H1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on T1: Use I2 for liquids + G1 for solids -Abigayle Hodson
Note on U1: Use I2 for liquids + calculate biogas based on influent COD linear regression, assume all DG goes to CHP -Abigayle Hodson
Note on V1: Use I3 for liquids (excluding lime) and B5 for solids- modified gravity thickener -Abigayle Hodson
Note on W1: Use I3 for liquids (excluding lime) and B6 for solids- modified gravity thickener -Abigayle Hodson
Note on X1: Use N1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on Y1: Use O1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on Z1: Use O1 for liquids + E2P for solids -Abigayle Hodson
Note on AA1: Use O1 for liquids + average of O5 and O6 for solids, excluding incineration (no longer relevant) and lime stabilization (calculated using average dosing rate) -Abigayle Hodson
Note on AB1: Use O1 for liquids and B5 for solids -Abigayle Hodson
Note on AC1: Use O1 for liquids and B6 for solids -Abigayle Hodson
Note on C8: Average natural gas use for lime production -Abigayle Hodson
Note on K8: Average natural gas use for lime production -Abigayle Hodson
Note on P8: Average natural gas use for lime production -Abigayle Hodson
Note on AA8: Average natural gas use for lime production -Abigayle Hodson

## Frankentrains (Natural Gas) SA
| B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
All values in MJ/d
DG to CHP | 0 | 0 | 0 | 48702 | 0 | 0 | 0 | 49300 | 0 | 0 | 0 | 0 | 62900 | 0 | 0 | 0 | 0 | 60700 | 0 | 20710 | 0 | 0 | 70400 | 68500 | 0 | 0 | 0 | 0
DG to Boiler | 0 | 0 | 28625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NG to Boiler | 6250 | 6250 | 0 | 0 | 6250 | 6250 | 6250 | 0 | 6250 | 6250 | 6250 | 6250 | 0 | 6250 | 6250 | 6250 | 6250 | 0 | 0 | 0 | 6250 | 6250 | 0 | 0 | 6250 | 6250 | 6250 | 6250
Fuel Used for Chemical Production (Acetic Acid) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82506 | 82506 | 82506 | 82506 | 33662 | 0 | 0 | 0 | 0 | 220015 | 0 | 0 | 0 | 0 | 0
Fuel Used for Chemical Production (Methanol) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel Used for Chemical Production (Lime) | 0 | 5363.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5363.1679 | 0 | 0 | 0 | 0 | 5363.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5363.1679 | 0 | 0
Natural Gas to Direct Dryer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Natural Gas to Incinerator | 0 | 0 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 61271 | 19659 | 0 | 0 | 0 | 0 | 61271 | 19659
Total Natural Gas Usage | 6250 | 11613.1679 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 11613.1679 | 67521 | 25909 | 0 | 88756 | 94119.1679 | 150027 | 108415 | 33662 | 0 | 0 | 67521 | 25909 | 220015 | 0 | 6250 | 11613.1679 | 67521 | 25909
Imported Natural Gas, excluding chemicals | 6250 | 6250 | 0 | 0 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 6250 | 6250 | 67521 | 25909 | 0 | 0 | 0 | 67521 | 25909 | 0 | 0 | 6250 | 6250 | 67521 | 25909
Note on B1: Use B1 for liquids + E2P for solids -Abigayle Hodson
Note on C1: Use averaged of B5 and B6 for liquids and solids except for incineration (no longer relevant) and lime production from TT w/ lowest theoretical energy use (B1) -Abigayle Hodson
Note on D1: Use C3 for liquids (minus lime), B1 for solids, and TT w/ lowest AnD energy use for AnD (B1) -Abigayle Hodson
Note on E1: Use C1 for liquids + calculate biogas based on influent COD linear regression (low), assume all DG goes to CHP -Abigayle Hodson
Note on F1: Use C3 for liquids (minus lime) + N2 for solids -Abigayle Hodson
Note on G1: Use C3 for liquids (minus lime) and B5 for solids -Abigayle Hodson
Note on H1: Use C3 for liquids (minus lime) and B6 for solids -Abigayle Hodson
Note on I1: Use D1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on J1: Use D1 for liquids + N2 for solids -Abigayle Hodson
Note on K1: Use D1 for liquids and an average of D5 and D6 for solids, excluding incineration (no longer relevant) and lime stabilization from TT w/ lowest energy use (B1) -Abigayle Hodson
Note on L1: Use D1 for liquids and B5 for solids -Abigayle Hodson
Note on M1: Use D1 for liquids and B6 for solids -Abigayle Hodson
Note on N1: Use F1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on O1: Use G1 for liquids + E2P for solids -Abigayle Hodson
Note on P1: Use G1 for liquids + average of G5 and G6 for solids, excluding incineration (no longer relevant) and lime stabilization from TT w/ lowest energy use (B1) -Abigayle Hodson
Note on Q1: Use G1 for liquids and B5 for solids -Abigayle Hodson
Note on R1: Use G1 for liquids and B6 for solids -Abigayle Hodson
Note on S1: Use H1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on T1: Use I2 for liquids + G1 for solids + AnD w/ lowest energy use (B1) -Abigayle Hodson
Note on U1: Use I2 for liquids + G1E for solids + digester gas calculated from influent COD linear regression (low) -Abigayle Hodson
Note on V1: Use I3 for liquids (minus lime) and B5 for solids -Abigayle Hodson
Note on W1: Use I3 for liquids (minus lime) and B6 for solids -Abigayle Hodson
Note on X1: Use N1 for liquids + biogas, assume all DG goes to CHP -Abigayle Hodson
Note on Y1: Use O1 for liquids and O1 for solids processing -Abigayle Hodson
Note on Z1: Use O1 for liquids + E2P for solids -Abigayle Hodson
Note on AA1: Use O1 for liquids + average of O5 and O6 for solids, excluding incineration (no longer relevant) and lime stabilization from TT w/ lowest energy use (B1) -Abigayle Hodson
Note on AB1: Use O1 for liquids and B5 for solids -Abigayle Hodson
Note on AC1: Use O1 for liquids and B6 for solids -Abigayle Hodson

## Decision Flow Chart
Liquid treatment train selection
1. Use overall liquid treatment train as a base (ie same letter)
2. If there is more than one option for liquid treatment trains, choose a train that is matched to the same solids treatment train group
Solids treatment train groups:
A. Dewatering after stabilization: anaerobic digestion, aerobic digestion
B. Dewatering before stabilization: lime stabilization, multiple hearth incinerator, fluidized bed incinerator
3. For lime stabilization in B3, where we have limited data availability, use the average of the two incinerator values for the biological reactor blower energy requirement.
Solids treatment train selection
1. Aerobic digestion
A. Use the liquid treatment train to determine the CODin to the digester. This will be the sum of the COD out of mechanical thickener (if present) and gravity thickener (if present)
B. Match energy values to a known treatment train based on closest alignment with CODin. Use these energy values for all inputs except aerobic digester energy
C. Calculate the energy requirement of the aerobic digester using the linear best equation for aerobic digester energy requirement as a function of CODin.
2. Anaerobic digestion
A. Because there isn't a linear relationship between CODin and energy use by anaerobic digestors, identify solids treatment process by clustering
3. Lime Stabilization
A. Use the average energy required to produce lime using the dosing rate and energy input for lime production (see Lime Stabilization tab)
B. For all non-lime stabilization processes, use an average of the 5 & 6 treatment trains energy use values. Upstream of lime stabilization or incineration, unit processes are the same with minimal variation in energy requried for unit processes (thickener + dewatering)
C. Where necessary, use the created Frankentrain 5 & 6 solids treatment values
4. MHI
A. Assume that electricity and fuel input to incinerator is a function of the cake concentration at the inlet
B. Because dewatering unit output stream is at a constant concentration, fuel & electricity content will likely not change substantial
C. Use B5 energy requirement for all created 5 trains
D. For treatment trains with both a gravity thickener and a mechanical thickener,
5. FBI

## AeD Frankentrains
Frankenstein TT | Liquids TT | Solids TT | CODin to Digester [MJ/d] | Electricity Consumed by AeD [kWh/d]
B2 | B1 | E2P | 126439 | 5284.3692
C2 | C3 | N2 | 109939 | 4248.1692
D2 | D1 | N2 | 108205 | 4139.274
G2 | G1 | E2P | 128460 | 5411.288
O2 | O1 | E2P | 128653 | 5423.4084
Note on B1: Select liquids TT based on existing trains with same letter -Abigayle Hodson
Note on C1: Select solids TT based on the closest CODin of known AeD trains -Abigayle Hodson
Note on D1: CODin to digester is based on liquids TT -Abigayle Hodson
Note on E1: The equation that relates CODin to electricity consumed is from linear best fit of known AeD trains -Abigayle Hodson

## AeD Sensitivity Analysis Plots
TT | Total COD | Electricity Consumed (kWh/d) | lower | upper | conf se
N/A | 75000 | 2053.5 | 1527.3843 | 2579.6157 | 165.318
N/A | 85000 | 2681.5 | 2280.6999 | 3082.3001 | 125.9409
N/A | 95000 | 3309.5 | 2975.6854 | 3643.3146 | 104.8925
N/A | 105000 | 3937.5 | 3578.0946 | 4296.9054 | 112.9337
N/A | 115000 | 4565.5 | 4103.0492 | 5027.9508 | 145.313
N/A | 125000 | 5193.5 | 4588.9358 | 5798.0642 | 189.9684
N/A | 135000 | 5821.5 | 5057.2464 | 6585.7536 | 240.1466
B2 | 126439 | 5283.8692 | 4657.1088 | 5910.6296 | 196.943
C2 | 109939 | 4247.6692 | 3844.3919 | 4650.9465 | 126.7193
D2 | 108205 | 4138.774 | 3752.7366 | 4524.8114 | 121.3021
G2 | 128460 | 5410.788 | 4752.34 | 6069.236 | 206.9
O2 | 128653 | 5422.9084 | 4761.4056 | 6084.4112 | 207.8599

## Aerobic Digester Best Fit
Treatment Train | Total COD | Electricity Consumed (kWh/d) | Electricity Consumed : COD |  | Treatment Train | Total COD | Electricity Consumed (kWh/d)
E2_T | 92463 | 3486 | 0.037702 | Base trains | E2_T | 92463 | 3486
E2P_T | 126908 | 5327 | 0.041975 |  | E2P_T | 126908 | 5327
I2_T | 75899 | 2045 | 0.026944 |  | I2_T | 75899 | 2045
N2_T | 107444 | 3915 | 0.036438 |  | N2_T | 107444 | 3915
N2P_T | 84037 | 2502 | 0.029773 |  | N2P_T | 84037 | 2502
|  |  |  | Created trains | B2 | 126439 | 5284.3692 | 0.041794
[5 empty] | C2 | 109939 | 4248.1692 | 0.038641
[5 empty] | D2 | 108205 | 4139.274 | 0.038254
[5 empty] | G2 | 128460 | 5411.288 | 0.042124
[5 empty] | O2 | 128653 | 5423.4084 | 0.042155

## Anaerobic Electricity Use
TT | Reactor Volume (MG) | Electricity Use [kWh / day] | DG to Boiler
A1 | 0.85 | 1288 | 30375
B1 | 0.85 | 1217 | 28625
B1E | 0.85 | 1217 | -
D1 | 0.9 | 1288 | 28500
F1 | 0.85 | 1217 | 29625
O1 | 0.9 | 1288 | 30375
G1 | 0.95 | 1575 | 32750
G1E | 0.95 | 1575
H1 | 1.1 | 1575 | 34250
N1 | 1.2 | 1575
P1 | 0.89 | 1217 | 30375
P1E | 0.89 | 1217
L1 |  |  | 38000
M1 |  |  | 37250
N1 |  |  | 37125
TT | CODin 1 (MJ/d) | CODin 2 (MJ/d) | Total COD in | Electricity Use [kWh / day] | DG to Boiler
A1 | 129836 | 0 | 129836 | 1288 | 30375
B1 | 47302 | 79137 | 126439 | 1217 | 28625
B1E | 47317 | 79138 | 126455 | 1217 | -
D1 | 108205 | 0 | 108205 | 1288 | 28500
F1 | 46735 | 79438 | 126173 | 1217 | 29625
O1 | 128653 | 0 | 128653 | 1288 | 30375
G1 | 48925 | 79535 | 128460 | 1575 | 32750
G1E | 48927 | 79535 | 128462 | 1575
H1 | 44028 | 82400 | 126428 | 1575 | 34250
N1 | 148796 | 0 | 148796 | 1575
P1 | 132100 | 0 | 132100 | 1217 | 30375
P1E | 132104 | 0 | 132104 | 1217
L1 |  |  |  |  | 38000
M1 |  |  |  |  | 37250
N1 |  |  |  |  | 37125
TT | Total COD in | DG to Boiler
A1 | 129836 | 30375
B1 | 126439 | 28625
D1 | 108205 | 28500
F1 | 126173 | 29625
O1 | 128653 | 30375
G1 | 128460 | 32750
H1 | 126428 | 34250
P1 | 132100 | 30375
P1E | 132104
38000
37250
37125

## Biogas Linear Regression
FIxed y int
Typical values | COD influent [MJ/d] | Digester Gas Production (MJ/d) |  | COD influent [MJ/d] | Digester Gas Production (MJ/d) | lower | upper | conf se
|  |  |  | 75899 | 45986 | 20710.1448 | 71261.8552 | 11600.7464
A1 | 129836 | 69300 |  | 115000 | 60343 | 52772.4792 | 67913.5208 | 3474.6082
B1 | 126439 | 68300 |  | 116000 | 60710 | 53566.7028 | 67853.2972 | 3278.5272
B1E | 126455 | 68300 |  | 117000 | 61077 | 54356.2205 | 67797.7795 | 3084.6062
F1 | 126173 | 62900 |  | 118000 | 61444 | 55140.086 | 67747.914 | 2893.2793
G1 | 128460 | 62400 |  | 119000 | 61811 | 55917.0998 | 67704.9002 | 2705.0971
G1E | 128462 | 62300 |  | 120000 | 62178 | 56685.7273 | 67670.2727 | 2520.7639
L1 | 133429 | 61100 |  | 121000 | 62546 | 57444.987 | 67647.013 | 2341.1892
M1 | 131405 | 61300 |  | 122000 | 62913 | 58190.3016 | 67635.6984 | 2167.5558
N1 | 148796 | 70400 |  | 123000 | 63280 | 58919.3006 | 67640.6994 | 2001.4107
N1P | 119999 | 56000 |  | 124000 | 63647 | 59627.5733 | 67666.4267 | 1844.7784
O1 | 128653 | 68600 |  | 125000 | 64014 | 60309.3871 | 67718.6129 | 1700.2896
P1 | 132100 | 73000 |  | 126000 | 64381 | 60957.4354 | 67804.5646 | 1571.2982
P1E | 132104 | 73000 |  | 127000 | 64749 | 61563.7676 | 67934.2324 | 1461.9119
B4 | 126439 | 68300 |  | 128000 | 65116 | 62116.1852 | 68115.8148 | 1376.8116
|  |  |  | 129000 | 65483 | 62605.441 | 68360.559 | 1320.7004
Source of equations: https://real-statistics.com/regression/confidence-and-prediction-intervals/plots-regression-confidence-prediction-intervals/ |  |  |  | 130000 | 65850 | 63023.3279 | 68676.6721 | 1297.3451
|  |  |  | 131000 | 66217 | 63366.0217 | 69067.9783 | 1308.5008
alpha | 0.05 |  |  | 132000 | 66584 | 63635.3812 | 69532.6188 | 1353.3144
n | 14 |  |  | 133000 | 66952 | 63839.3001 | 70064.6999 | 1428.622
mean(x) | 130177.77 |  |  | 134000 | 67319 | 63985.5751 | 70652.4249 | 1529.9272
devsq(x) | 521939698.3 |  |  | 135000 | 67686 | 64085.6089 | 71286.3911 | 1652.4554
steyx | 4852.1647 |  |  | 136000 | 68053 | 64148.8762 | 71957.1238 | 1791.8583
t-crit | 2.1788 |  |  | 137000 | 68420 | 64183.2769 | 72656.7231 | 1944.5099
|  |  |  | 138000 | 68787 | 64195.0794 | 73378.9206 | 2107.5333
|  |  |  | 139000 | 69155 | 64190.1314 | 74119.8686 | 2278.7036
|  |  |  | 140000 | 69522 | 64170.1425 | 74873.8575 | 2456.3181
|  |  |  | 141000 | 69889 | 64138.947 | 75639.053 | 2639.0762
|  |  |  | 142000 | 70256 | 64098.7186 | 76413.2814 | 2825.9799
|  |  |  | 143000 | 70623 | 64051.1364 | 77194.8636 | 3016.2589
|  |  |  | 144000 | 70991 | 63998.5083 | 77983.4917 | 3209.3127
|  |  |  | 145000 | 71358 | 63939.8625 | 78776.1375 | 3404.6694
|  |  |  | 146000 | 71725 | 63877.0156 | 79572.9844 | 3601.9544
|  |  |  | 147000 | 72092 | 63810.6216 | 80373.3784 | 3800.8673
|  |  |  | 148000 | 72459 | 63741.2096 | 81176.7904 | 4001.1653
|  |  |  | 149000 | 72826 | 63669.2111 | 81982.7889 | 4202.6505
|  |  |  | 150000 | 73194 | 63595.9809 | 82792.0191 | 4405.16
|  |  |  | 151000 | 73561 | 63519.8133 | 83602.1867 | 4608.5586
|  |  |  | 152000 | 73928 | 63441.9539 | 84414.0461 | 4812.7338
|  |  | I1E | 75899 | 45986
|  |  | C1E | 109939 | 58484
|  |  | D1E | 108205 | 49300
|  |  | F1E | 126173 | 62900
|  |  | H1E | 126428 | 60700
|  |  | N1E | 148796 | 70400
|  |  | O1E | 128653 | 68500

## Generator Efficiency
Generator Efficiency
Treatment Train | Typical (kWh / MG) - as reported | Best Practice (kWh / MG) - as reported | Typical (kWh / MJ biogas input) - calculated | Best Practice (kWh / MJ biogas input) - calculated
B1E | 631 | 810 | 0.092387 | 0.11081
G1E | 576 | 785 | 0.092456 | 0.11072
P1E | 675 | 818 | 0.092466 | 0.11084

## Lime Production
TT | Typical Cake Concentration [mg/L] | Best Practice [mg/L] |  | Typical Cake Flow Rate [MGD] | Best Practice [MGD] | Typical Cake Mass [kg TSS/day] | Typical Cake Weight [lbs TSS/day] | Lime Dose [lbs lime/lbs TSS] | Electricity [kWh/d] | Natural Gas [MJ/d]
A1 | 180000 | 230000 |  | 0.006379 | 0.004903 | 4346.4835 | 9582.3444 | 0.25001 | 67.2132 | 5586.4872 | Expected Energy Requirement
A5 (B5) | 200000 | 250000 |  | 0.010781 | 0.008887 | 8162.101 | 17994.3312 | 0.25001 | 126.2172 | 10490.6584 |  | Electricity (kWh/d) | Natural Gas (MJ / day)
A6 (B6) | 200000 | 250000 |  | 0.010774 | 0.008873 | 8156.8015 | 17982.6477 | 0.25001 | 126.1353 | 10483.8469 | Mean | 86.5979 | 7294.1033
B1 | 180000 | 230000 |  | 0.006124 | 0.0047681 | 4172.7332 | 9199.291 | 0.25001 | 64.5264 | 5363.1679 | Minimum | 64.5264 | 5363.1679
B1E | 180000 | 230000 |  | 0.006124 | 0.004769 | 4172.7332 | 9199.291 | 0.25001 | 64.5264 | 5363.1679 | Maximum | 126.2172 | 10490.6584
B4 | 180000 | 230000 |  | 0.006124 | 0.004769 | 4172.7332 | 9199.291 | 0.25001 | 64.5264 | 5363.1679 | Standard Deviation | 21.6032 | 1793.9653
E2 | 200000 | 200000 |  | 0.005933 | 0.005931 | 4491.7675 | 9902.6405 | 0.25001 | 69.4599 | 5773.2192
E2P | 200000 |  |  | 0.006963 |  | 5271.562 | 11621.7909 | 0.25001 | 81.5185 | 6775.4804
F1 | 180000 |  |  | 0.006613 |  | 4505.9249 | 9933.8522 | 0.25001 | 69.6788 | 5791.4156
G1 | 180000 |  |  | 0.007583 |  | 5166.8575 | 11390.9574 | 0.25001 | 79.8993 | 6640.905
G1E | 180000 |  |  | 0.007582 |  | 5166.1762 | 11390.1425 | 0.25001 | 79.8936 | 6640.4298
H1 | 204475.6 |  |  | 0.008 |  | 6192.1918 | 13651.43 | 0.25001 | 95.7549 | 7958.7558
I2 | 170000 |  |  | 0.006749 |  | 4343.1145 | 9574.917 | 0.25001 | 67.1611 | 5582.1571
I3 | 170000 |  |  | 0.008679 |  | 5585.1075 | 12313.0396 | 0.25001 | 86.3671 | 7178.477
L1 | 180000 |  |  | 0.011132 |  | 7585.0531 | 16722.1599 | 0.25001 | 117.2938 | 9748.9851
M1 | 180000 |  |  | 0.010845 |  | 7389.4989 | 16291.037 | 0.25001 | 114.2698 | 9497.6413
N1 | 180000 |  |  | 0.009101 |  | 6201.183 | 13671.252 | 0.25001 | 95.8939 | 7970.312
N2 | 170000 |  |  | 0.008886 |  | 5718.3161 | 12606.7139 | 0.25001 | 88.427 | 7349.6885
C3 | [8 empty] | 109 | 9030
I3 | 170000 |  |  | 0.008679 |  | 5585.1075 | 12313.0396 | 0.25001 | 86 | 7178
Average | [8 empty] | 87.777 | 7294.1033
UNIT CONVERSIONS
| Liquid volume |  |  | Liters / gallon |  | 3.7854
| Mass |  |  | Pounds / kg |  | 2.2046
REPORTED IN WERF
| Lime dosing |  |  | lb / ton wet weight |  | 85
| Electricity Used for Chemical Production | kWh/lb | 0.028056 | kWh/lb |  | 0.028056
| Fuel Used for Chemical Production | MJ/lb | 2.3319 | MJ/lb |  | 2.3319
I3 LIME CALCULATIONS
| Reported Fuel Used for Chemical Production | MJ/day | 7178.477 | MJ/day |  | 7178.477
| Reported Electricity Used for Chemical Production |  |  | kWh/day |  | 86.3657
| Calculated lime production / day - using electricity |  |  | lbs lime / day |  | 3078.3326
| Calculated lime production / day - using fuel |  |  | lbs lime / day |  | 3078.3811
| Reported cake production |  |  | lbs TSS / day |  | 12313.0396
| Calculated lime dose |  |  | lbs lime / lb TSS |  | 0.25001
Note on B1: All entries from the "Cake" column, TSS in mg / L from WERF documentation in the MB_&_HB spreadsheet. Originally compiled by Sahar + Abby, double checked by Sahar on 6/10/24 -Sahar El Abbadi
Note on E1: All entries from the "Cake" column, flow in MGD, from WERF documentation in the MB_&_HB spreadsheet. Originally compiled by Sahar + Abby, double checked by Sahar on 6/10/24 -Sahar El Abbadi
Note on B34: Where did this come from? -Sahar El Abbadi

## Thickener
All values in kWh/day | Gravity Thickener | Mechanical Thickener | Configuration | Gravity Thickener Energy | Mechanical Thickener Energy
A1 | 27 | 0 | Gravity Thickener Only | 27.5 | 0
B1 | 23 | 156 | Mechanical Thickener Only | 0 | 162.2857
B1E | 23 | 156 | Both Thickeners Present | 24.0833 | 155.75
B4 | 23 | 156
B5 | 25 | 157
B6 | 25 | 141
C3 | 0 | 163
D1 | 26 | 0
E2 | 0 | 161
E2P | 25 | 156
F1 | 23 | 157
G1 | 23 | 158
G1E | 23 | 158
H1 | 25 | 157
i2 | 0 | 160
i3 | 0 | 160
L1 | 25 | 159
M1 | 26 | 158
N1 | 30 | 0
N2 | 0 | 164
O1 | 27 | 0
P1 | 0 | 164
P1E | 0 | 164

## Sahar - cake plots (hidden)
TT | Typical Cake Concentration [mg/L]
I2 | 170000
I3 | 170000
N2 | 170000
A1 | 180000
B1 | 180000
B1E | 180000
B4 | 180000
F1 | 180000
G1 | 180000
G1E | 180000
L1 | 180000
M1 | 180000
N1 | 180000
A5 (B5) | 200000
A6 (B6) | 200000
E2 | 200000
E2P | 200000
H1 | 204475.6
TT | Typical Cake Flow Rate [MGD]
I2 | 0.006749
I3 | 0.008679
N2 | 0.008886
A1 | 0.006379
B1 | 0.006124
B1E | 0.006124
B4 | 0.006124
F1 | 0.006613
G1 | 0.007583
G1E | 0.007582
L1 | 0.011132
M1 | 0.010845
N1 | 0.009101
A5 (B5) | 0.010781
A6 (B6) | 0.010774
E2 | 0.005933
E2P | 0.006963
H1 | 0.008