## All Trains (For Code)
| B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Total Electricity Usage [kWh/d] | 9479 | 9479 | 10748 | 12135 | 10792 | 11134 | 8903 | 14355 | 13531 | 11333 | 15645 | 15645 | 13226 | 15102 | 14347 | 15359 | 14199 | 37255 | 36734 | 12300 | 13409 | 13408 | 12293.3477 | 9670.8143 | 10956.8571 | 10956.8571 | 13174.1007 | 13540.8571 | 12227.8571 | 8903 | 11411.6561 | 9040.3143 | 11488 | 10175 | 11333 | 18574.0781 | 15748.8143 | 18196.5 | 16883.5 | 13226 | 14049.8571 | 14049.8571 | 16813.8571 | 15500.8571 | 37255 | 12300 | 15179.8419 | 12436.3143 | 14884 | 13571
CHP Electricity Generation [kWh/d] |  | 8100 | [9 empty] | 7850 | [9 empty] | 8180 |  |  |  | 6341.0847 |  |  |  | 6260.2 |  |  |  |  | 7700.6 |  |  |  |  | 7578.72 |  | 4412.4063 |  |  | 8864 | 8254.6
Total Natural Gas Usage [MJ/d] | 0 | 0 | 0 | 42414 | 5952 | 15064 | 0 | 5952 | 5952 | 0 | 96257 | 96257 | 41583 | 5952 | 13212 | 119845 | 87898 | 220015 | 143461 | 0 | 0 | 0 | 5952 | 13209.1076 | 0 | 0 | 5952 | 42414 | 5952 | 0 | 5952 | 13209.1076 | 42414 | 5952 | 0 | 102209 | 109466.1076 | 138671 | 102209 | 41583 | 0 | 0 | 42414 | 5952 | 220015 | 0 | 5952 | 13209.1076 | 42414 | 5952

## WERF Trains (Electricity)
All values in kWh/day | B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E
Total Net Electricity Import
Electricity Usage by Process
Liquid Stream Processes | 5308 | 5308 | 5308 | 5377 | 5347 | 6803 | 4885 | 8156 | 6674 | 7162 | 11440 | 11440 | 9020 | 9863 | 10076 | 11185 | 10026 | 33202 | 30362 | 8281 | 9254 | 9253
Influent Pump Station | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1812 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480
Screening and Grit Removal | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Primary Clarifiers | 97 | 97 | 97 | 99 | 99 |  | 99 |  | 99 | 98 | 98 | 98 | 101 |  |  | 98 | 101 | 99 |  | 99
Biological Reactor Blowers | 2086 | 2086 | 2086 | 2146 | 2116 | 3640 |  | 5187 | 3646 | 4135 | 4943 | 4943 | 4642 | 6904 | 6923 | 4795 | 4726 |  |  | 5053 | 5251 | 5250
Final Clarifiers + RAS Pumping | 745 | 745 | 745 | 752 | 752 | 783 | 91 | 783 | 743 | 743 | 485 | 485 | 481 | 773 | 773 | 494 | 490 |  |  | 749 | 1623 | 1623
Trickling Filter | [6 empty] | 1344
TF Recycle Pump | [6 empty] | 444
MBR Effluent Pump | [17 empty] | 22396 | 22850
Denite Filter | [15 empty] | 888 | 888
Disinfection | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Hypchlorite Production | 778 | 778 | 778 | 778 | 778 | 778 | 973 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 778 | 584 | 584 | 584 | 584 | 778 | 778 | 778
Acetic Acid Production | [10 empty] | 3728 | 3728 | 1610 |  |  | 2724 | 1635 | 8521 | 5326
Solids Processes | 371 | 371 | 1640 | 2958 | 1645 | 531 | 218 | 2399 | 3057 | 371 | 405 | 405 | 406 | 1439 | 471 | 374 | 373 | 253 | 2572 | 219 | 355 | 355
Gravity Thickener | 21 | 21 | 21 | 23 | 23 |  | 22 |  | 23 | 21 | 21 | 21 | 22 |  |  | 22 | 22 | 24 |  | 23
Mechanical Thickener | 154 | 154 | 154 | 155 | 155 | 158 |  | 157 | 155 | 154 | 155 | 155 | 155 | 157 | 157 | 156 | 155 |  | 158 |  | 159 | 159
Anaerobic Digestion | 107 | 107 | 107 |  |  |  | 107 |  |  | 107 | 140 | 140 | 140 |  |  | 107 | 107 | 140 |  | 107 | 107 | 107
Aerobic Digestion | [7 empty] | 2153 | 2790 |  |  |  |  | 1193 |  |  |  |  | 2325
Dewatering | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Sidestream Pump
Incineration |  |  |  | 2691 | 1378
Dryer |  |  | 1269
Lime Stabilization | [5 empty] | 174 | [8 empty] | 138
Lime Production | [5 empty] | 110 | [8 empty] | 87
Plant-wide | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
Odor Control | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Site Lighting & Misc. | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
Total Electricity Usage | 9479 | 9479 | 10748 | 12135 | 10792 | 11134 | 8903 | 14355 | 13531 | 11333 | 15645 | 15645 | 13226 | 15102 | 14347 | 15359 | 14199 | 37255 | 36734 | 12300 | 13409 | 13408
CHP Electricity Generation |  | 8100 | [9 empty] | 7850 | [9 empty] | 8180
Net Electricity Import | 9479 | 1379 | 10748 | 12135 | 10792 | 11134 | 8903 | 14355 | 13531 | 11333 | 15645 | 7795 | 13226 | 15102 | 14347 | 15359 | 14199 | 37255 | 36734 | 12300 | 13409 | 5228

## Frankentrains (Electricity)
All values in kWh/day | B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
Electricity Usage by Process
Liquid Stream Processes | 5308 | 5362 | 6803 | 6803 | 6803 | 6803 | 6803 | 4885 | 4885 | 4885 | 4885 | 4885 | 7162 | 11440 | 11440 | 11440 | 11440 | 9020 | 9863 | 9863 | 10076 | 10076 | 33202 | 8281 | 8281 | 8281 | 8281 | 8281
Influent Pump Station | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1812 | 1812 | 1812 | 1812 | 1812 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480 | 1480
Screening and Grit Removal | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Primary Clarifiers | 97 | 99 | [5 empty] | 99 | 99 | 99 | 99 | 99 | 98 | 98 | 98 | 98 | 98 | 101 |  |  |  |  | 99 | 99 | 99 | 99 | 99 | 99
Biological Reactor Blowers | 2086 | 2131 | 3640 | 3640 | 3640 | 3640 | 3640 | [5 empty] | 4135 | 4943 | 4943 | 4943 | 4943 | 4642 | 6904 | 6904 | 6923 | 6923 |  | 5053 | 5053 | 5053 | 5053 | 5053
Final Clarifiers + RAS Pumping | 745 | 752 | 783 | 783 | 783 | 783 | 783 | 91 | 91 | 91 | 91 | 91 | 743 | 485 | 485 | 485 | 485 | 481 | 773 | 773 | 773 | 773 |  | 749 | 749 | 749 | 749 | 749
Trickling Filter | [7 empty] | 1344 | 1344 | 1344 | 1344 | 1344
TF Recycle Pump | [7 empty] | 444 | 444 | 444 | 444 | 444
MBR Effluent Pump | [22 empty] | 22396
Denite Filter
Disinfection | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Hypochlorite Production | 778 | 778 | 778 | 778 | 778 | 778 | 778 | 973 | 973 | 973 | 973 | 973 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 584 | 778 | 778 | 584 | 778 | 778 | 778 | 778 | 778
Acetic Acid Production | [13 empty] | 3728 | 3728 | 3728 | 3728 | 1610 |  |  |  |  | 8521
Solids Processes | 3185.3477 | 508.8143 | 353.8571 | 353.8571 | 2571.1007 | 2937.8571 | 1624.8571 | 218 | 2726.6561 | 355.3143 | 2803 | 1490 | 371 | 3334.0781 | 508.8143 | 2956.5 | 1643.5 | 406 | 386.8571 | 386.8571 | 2937.8571 | 1624.8571 | 253 | 219 | 3098.8419 | 355.3143 | 2803 | 1490
Gravity Thickener | 21.75 | 21.75 | [5 empty] | 22 |  | 23 | 23 | 23 | 21 | 21.75 | 21.75 | 21.75 | 21.75 | 22 |  |  |  |  | 24 | 23 | 23 | 23 | 23 | 23
Mechanical Thickener | 154.75 | 154.75 | 157.8571 | 157.8571 | 157.8571 | 157.8571 | 157.8571 |  | 157.8571 |  |  |  | 154 | 154.75 | 154.75 | 154.75 | 154.75 | 155 | 157.8571 | 157.8571 | 157.8571 | 157.8571
Anaerobic Digestion |  |  | 107 | 107 |  |  |  | 107 |  |  |  |  | 107 |  |  |  |  | 140 | 140 | 140 |  |  | 140 | 107
Aerobic Digestion | 2919.8477 |  |  |  | 2324.2436 |  |  |  | 2479.799 |  |  |  |  | 3068.5781 | [10 empty] | 2986.8419
Dewatering | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89
Sidestream Pump
Incineration | [5 empty] | 2691 | 1378 |  |  |  | 2691 | 1378 |  |  |  | 2691 | 1378 |  |  |  | 2691 | 1378 |  |  |  |  | 2691 | 1378
Dryer
Lime Stabilization |  | 156 | [7 empty] | 156 |  |  |  |  | 156 | [10 empty] | 156
Lime Production |  | 87.3143 | [7 empty] | 87.3143 |  |  |  |  | 87.3143 | [10 empty] | 87.3143
Plant-wide | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
Odor Control | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
Site Lighting & Misc. | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
Total Electricity Usage | 12293.3477 | 9670.8143 | 10956.8571 | 10956.8571 | 13174.1007 | 13540.8571 | 12227.8571 | 8903 | 11411.6561 | 9040.3143 | 11488 | 10175 | 11333 | 18574.0781 | 15748.8143 | 18196.5 | 16883.5 | 13226 | 14049.8571 | 14049.8571 | 16813.8571 | 15500.8571 | 37255 | 12300 | 15179.8419 | 12436.3143 | 14884 | 13571
CHP Electricity Generation |  |  |  | 6341.0847 |  |  |  | 6260.2 |  |  |  |  | 7700.6 |  |  |  |  | 7578.72 |  | 4412.4063 |  |  | 8864 | 8254.6
Net Electricity Import | 12293.3477 | 9670.8143 | 10956.8571 | 4615.7724 | 13174.1007 | 13540.8571 | 12227.8571 | 2642.8 | 11411.6561 | 9040.3143 | 11488 | 10175 | 3632.4 | 18574.0781 | 15748.8143 | 18196.5 | 16883.5 | 5647.28 | 14049.8571 | 9637.4508 | 16813.8571 | 15500.8571 | 28391 | 4045.4 | 15179.8419 | 12436.3143 | 14884 | 13571

## WERF Trains (Natural Gas)
| B1 | B1E | B4 | B5 | B6 | C3 | D1 | E2 | E2P | F1 | G1 | G1E | H1 | I2 | I3 | L1 | M1 | N1 | N2 | O1 | P1 | P1E
All values in MJ/d
DG to CHP |  | 73100 | [9 empty] | 70900 | [9 empty] | 73800
DG to Boiler | 23929 |  | 23929 |  |  |  | 22857 |  |  | 23929 | 26786 |  | 27500 |  |  | 30595 | 31125 | 28690 |  | 24048 | 25238
NG to Boiler |  |  |  | 5952 | 5952 | 5952 |  | 5952 | 5952 |  |  |  |  | 5952 | 5952 |  |  |  | 5952
Fuel Used for Chemical Production (Acetic Acid) | [10 empty] | 96257 | 96257 | 41583 |  |  | 70342 | 42205 | 220015 | 137509
Fuel Used for Chemical Production (Methanol) | [15 empty] | 49503 | 45693
Fuel Used for Chemical Production (Lime) | [5 empty] | 9112 | [8 empty] | 7260
Natural Gas to Direct Dryer
Natural Gas to Incinerator |  |  |  | 36462
Total Natural Gas Usage | 0 | 0 | 0 | 42414 | 5952 | 15064 | 0 | 5952 | 5952 | 0 | 96257 | 96257 | 41583 | 5952 | 13212 | 119845 | 87898 | 220015 | 143461 | 0 | 0 | 0

## Frankentrains (Natural Gas)
| B2 | B3 | C1 | C1E | C2 | C5 | C6 | D1E | D2 | D3 | D5 | D6 | F1E | G2 | G3 | G5 | G6 | H1E | I1 | I1E | I5 | I6 | N1E | O1E | O2 | O3 | O5 | O6
All values in MJ/d
DG to CHP |  |  |  | 57230.0064 |  |  |  | 56500 |  |  |  |  | 69500 |  |  |  |  | 68400 |  | 39823.1616 |  |  | 80000 | 74500
DG to Boiler |  |  | 23929 | [15 empty] | 26786
NG to Boiler | 5952 | 5952 |  |  | 5952 | 5952 | 5952 |  | 5952 | 5952 | 5952 | 5952 |  | 5952 | 5952 | 5952 | 5952 |  |  |  | 5952 | 5952 |  |  | 5952 | 5952 | 5952 | 5952
Fuel Used for Chemical Production (Acetic Acid) | [13 empty] | 96257 | 96257 | 96257 | 96257 | 41583 |  |  |  |  | 220015
Fuel Used for Chemical Production (Methanol)
Fuel Used for Chemical Production (Lime) |  | 7257.1076 | [7 empty] | 7257.1076 |  |  |  |  | 7257.1076 | [10 empty] | 7257.1076
Natural Gas to Direct Dryer
Natural Gas to Incinerator | [5 empty] | 36462 |  |  |  |  | 36462 |  |  |  |  | 36462 |  |  |  |  | 36462 | [5 empty] | 36462
Total Natural Gas Usage | 5952 | 13209.1076 | 0 | 0 | 5952 | 42414 | 5952 | 0 | 5952 | 13209.1076 | 42414 | 5952 | 0 | 102209 | 109466.1076 | 138671 | 102209 | 41583 | 0 | 0 | 42414 | 5952 | 220015 | 0 | 5952 | 13209.1076 | 42414 | 5952
Imported Natural Gas, including chemicals | 5952 | 13209.1076 | 0 | 0 | 5952 | 42414 | 5952 | 0 | 5952 | 13209.1076 | 42414 | 5952 | 0 | 102209 | 109466.1076 | 138671 | 102209 | 41583 | 0 | 0 | 42414 | 5952 | 220015 | 0 | 5952 | 13209.1076 | 42414 | 5952
Imported Natural Gas, excluding chemicals | 5952 | 5952 | 0 | 0 | 5952 | 42414 | 5952 | 0 | 5952 | 5952 | 42414 | 5952 | 0 | 5952 | 5952 | 42414 | 5952 | 0 | 0 | 0 | 42414 | 5952 | 0 | 0 | 5952 | 5952 | 42414 | 5952

## Biogas Linear Regression
Best practice values | COD influent [MJ/d] | Digester Gas Production (MJ/d)
B1 | 128749 | 73100
B1E | 128750 | 73100
D1 | 112630 | 56500
F1 | 129294 | 69500
G1 | 134288 | 70700
G1E | 128462 | 62300
H1 | 131140 | 68400
L1 | 140215 | 70600
M1 | 135571 | 68800
N1 | 153247 | 80000
N1P | 124662 | 64400
O1 | 131203 | 74500
P1 | 129612 | 73800
P1E | 129612 | 73800
B4 | 128752 | 73100
I1E | 74408 | 39823.1616
C1E | 106932 | 57230.0064
D1E | 112630 | 56500
F1E | 129294 | 69500
H1E | 131140 | 68400
N1E | 153247 | 80000
O1E | 131203 | 74500

## Decision Flow Chart
Liquid treatment train selection
1. Use overall liquid treatment train as a base (ie same letter)
2. If there is more than one option for liquid treatment trains, choose a train that is matched to the same solids treatment train group
Solids treatment train groups:
A. Dewatering after stabilization: anaerobic digestion, aerobic digestion
B. Dewatering before stabilization: lime stabilization, multiple hearth incinerator, fluidized bed incinerator
3. For lime stabilization in B3, where we have limited data availability, use the average of the two incinerator values for the biological reactor blower energy requirement.
Solids treatment train selection
1. Aerobic digestion
A. Use the liquid treatment train to determine the CODin to the digester. This will be the sum of the COD out of mechanical thickener (if present) and gravity thickener (if present)
B. Match energy values to a known treatment train based on closest alignment with CODin. Use these energy values for all inputs except aerobic digester energy
C. Calculate the energy requirement of the aerobic digester using the linear best equation for aerobic digester energy requirement as a function of CODin.
2. Anaerobic digestion
A. Because there isn't a linear relationship between CODin and energy use by anaerobic digestors, identify solids treatment process by clustering
3. Lime Stabilization
A. Use the average energy required to produce lime using the dosing rate and energy input for lime production (see Lime Stabilization tab)
B. For all non-lime stabilization processes, use an average of the 5 & 6 treatment trains energy use values. Upstream of lime stabilization or incineration, unit processes are the same with minimal variation in energy requried for unit processes (thickener + dewatering)
C. Where necessary, use the created Frankentrain 5 & 6 solids treatment values
4. MHI
A. Assume that electricity and fuel input to incinerator is a function of the cake concentration at the inlet
B. Because dewatering unit output stream is at a constant concentration, fuel & electricity content will likely not change substantial
C. Use B5 energy requirement for all created 5 trains
D. For treatment trains with both a gravity thickener and a mechanical thickener,
5. FBI

## AeD Frankentrains
Frankenstein TT | Liquids TT | Solids TT | CODin to Digester [MJ/d] | Electricity Consumed by AeD [kWh/d]
B2 | B1 | E2P | 128749 | 2919.8477
C2 | C3 | N2 | 106932 | 2324.2436
D2 | D1 | N2 | 112630 | 2479.799
G2 | G1 | E2P | 134197 | 3068.5781
O2 | O1 | E2P | 131203 | 2986.8419

## Aerobic Digester Best Fit
Treatment Train | Total COD | Electricity Consumed (kWh/d)
E2_BP | 90431 | 2153
E2P_BP | 129967 | 2790
I2_BP | 74408 | 1193
N2_BP | 100587 | 2325
N2P_BP | 81113 | 1554

## Anaerobic Digester Clustering
TT | Reactor Volume (MG) | Electricity Use [kWh / day]
B1 | 0.85 | 107
B1E | 0.85 | 107
B4 |  | 107
D1 | 0.9 | 107
F1 | 0.85 | 107
O1 | 0.9 | 107
G1 | 0.95 | 140
G1E | 0.95 | 140
H1 | 1.1 | 140
N1 | 1.2 | 140
P1 | 0.89 | 107
P1E | 0.89 | 107

## Lime Production
TT | Typical Cake Weight [lbs TSS/day] | Lime Dose [lbs lime/lbs TSS] | Electricity [kWh/d] | Natural Gas [MJ/d]
A1 | 9411.7287 | 0.249 | 65.7508 | 5464.9365
A5 (B5) | 18542.3632 | 0.249 | 129.5378 | 10766.6552
A6 (B6) | 18512.0591 | 0.249 | 129.3261 | 10749.0591
B1 | 9152.0318 | 0.249 | 63.9365 | 5314.1431
B1E | 9153.2468 | 0.249 | 63.945 | 5314.8486
B4 | 9152.9698 | 0.249 | 63.9431 | 5314.6877
E2 | 9899.4933 | 0.249 | 69.1583 | 5748.1579
E2P | 11660.2972 | 0.249 | 81.4594 | 6770.5717
F1 | 9770.6942 | 0.249 | 68.2585 | 5673.3705
G1 | 11437.8574 | 0.249 | 79.9054 | 6641.4116
G1E | 11438.104 | 0.249 | 79.9071 | 6641.5548
H1 | 13573.4981 | 0.249 | 94.8251 | 7881.4751
I2 | 9333.2172 | 0.249 | 65.2023 | 5419.3487
L1 | 17629.3138 | 0.249 | 123.1592 | 10236.4915
M1 | 16193.9413 | 0.249 | 113.1316 | 9403.04
N1 | 13446.0109 | 0.249 | 93.9345 | 7807.4495
N2 | 10963.2719 | 0.249 | 76.5899 | 6365.8428
C3 | N/A | 0.249 | 110 | 9112
I3 | 12453.3932 | 0.249 | 87 | 7260
Average |  |  | 87.3143 | 7257.1076
Lime Quantity | lb/d | 3113.348
Electricity Used for Chemical Production | kWh/lb | 0.028056
Electricity Used for Chemical Production | kWh/day | 87.3467
Fuel Used for Chemical Production | MJ/lb | 2.3319
Fuel Used for Chemical Production | MJ/day | 7260.017

## Generator Efficiency
Generator Efficiency
Treatment Train | Typical (kWh / MG) - as reported | Best Practice (kWh / MG) - as reported | Typical (kWh / MJ biogas input) - calculated | Best Practice (kWh / MJ biogas input) - calculated
B1E | 631 | 810 | 0.092387 | 0.11081
G1E | 576 | 785 | 0.092456 | 0.11072
P1E | 675 | 818 | 0.092466 | 0.11084
0.11079

## Sahar - cake plots
TT | Typical Cake Concentration [mg/L]
I2 | 170000
I3 | 170000
N2 | 170000
A1 | 180000
B1 | 180000
B1E | 180000
B4 | 180000
F1 | 180000
G1 | 180000
G1E | 180000
L1 | 180000
M1 | 180000
N1 | 180000
A5 (B5) | 200000
A6 (B6) | 200000
E2 | 200000
E2P | 200000
H1 | 204475.6
TT | Typical Cake Flow Rate [MGD]
I2 | 0.006749
I3 | 0.008679
N2 | 0.008886
A1 | 0.006379
B1 | 0.006124
B1E | 0.006124
B4 | 0.006124
F1 | 0.006613
G1 | 0.007583
G1E | 0.007582
L1 | 0.011132
M1 | 0.010845
N1 | 0.009101
A5 (B5) | 0.010781
A6 (B6) | 0.010774
E2 | 0.005933
E2P | 0.006963
H1 | 0.008